BACnet TESTING LABORATORIES

INTERIM TEST FUNCTIONALITY CHECKLIST

To Be Used with Test Package 26.1

Version 2

March 19, 2026

Approved by the BTL Working Group March 19, 2026.

Approved by the BTL Working Group Voting Members May 11, 2026.

Published on May 14, 2026.

# Introduction

This checklist is in addition to the BTL Functionality Checklist and identifies the functionality beyond the Protocol_Revision of the released test package or functionality not yet tested by the current test package.

Vendors who are planning to submit a device at a Protocol_Revision beyond the Protocol_Revision of the released test package or includes functionality not yet tested by the current test package shall also complete this checklist.

Please note, the functionality implemented in a specific device may result in changes to this document as well as new or updated tests in the interim test package. Please contact the BTL Manager before submitting your device for testing to ensure you are aware of all tests that will need to be applied to your device.

The updates to the checklist specified in this document are for interim testing only and may or may not be used when the final changes are applied to the next Test Package revision. Devices tested using this interim test document may be recalled for updated testing when the next revision of test package is released that includes the functionality covered here.

The Listing column indicates whether the option is required or not. The codes in the table are:

R = Required. Items marked with this listing code are required for a listing if the IUT implements the associated BIBB, object type, or functional category.

BTL-R = Required by BTL. Items marked with this listing code are required for a listing if the IUT implements the associated BIBB, object type, or functional category.

C = Conditionally Required. Items marked with this listing code may be required for a listing if the IUT implements the associated BIBB, object type, or functional category. The conditions under which the item will be required are identified in a footnote in the Checklist table.

BTL-C = Conditionally Required by BTL. Items marked with this listing code may be required for a listing if the IUT implements the associated BIBB, object type, or functional category. The conditions under which the item will be required are identified in a footnote in the Checklist table.

S = Suggested. The BTL suggests that all IUTs implement this option if they implement the associated BIBB, object type, or functional category.

O = Optional. Items marked with this listing code are optional.

N = Not recommended. The BTL recommends against IUTs implementing this option due to possible interoperability or performance problems related with the option.

# IUT Information

This section shall provide additional information about the IUT when the BTL Checklist is filled out.

| Fill out date |  |
| --- | --- |
| Vendor Name |  |
| Product Name |  |
| Product Model Number |  |
| BACnet Protocol Version | 1 |
| BACnet Protocol Revision |  |
| BACnet Device Profile |  |
| BACnet Firmware Revision |  |
| BACnet Application Software Version |  |
| Remarks |  |

# 3 Objects

| … |  |  |
| --- | --- | --- |
| Lighting Output Object |  |  |
|  | R | Base Requirements |
|  | R | Supports command prioritization |
|  | R | Supports all BACnetLightingOperations |
|  | S | Supports configurable Out_Of_Service property |
|  | O | Supports blink-warn |
|  | O | Supports Transition property |
|  | O | Supports Feedback_Value property |
|  | O | Supports Min_Actual_Value and Max_Actual_Value properties |
|  | O | Supports the value source mechanism. |
|  | O1,3 | Supports Color_Reference property |
|  | O1 | Supports color override |
|  | O1,2 | Supports High_End_Trim or Low_End_Trim properties |
|  | O2 | Supports intrinsic reporting |
|  | O4 | Supports configurable Reliability_Evaluation_Inhibit property |
|  | O5,6 | Supports Last_On_Value and Default_On_Value properties |
| 1 Protocol_Revision 24 or higher must be claimed 2 Protocol_Revision 21 or higher must be claimed 3 Must be claimed if the IUT supports color override 4 Protocol_Revision 13 or higher must be claimed. IUT shall not claim this functionality if the only method of generating a fault condition is by writing to the Reliability property. 5 Required if the device claims Protocol_Revision of 28 or higher. 6 Contact BTL for interim tests for these properties. |  |  |
| Directory Object |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this object. |  |  |
| … |  |  |

# 8 Device Management BIBBs

| Support | Listing | Option |
| --- | --- | --- |
| … |  |  |
| Device Management - Device Address Proxying-View and Modify - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Device Management - Device Address Proxying - B |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Device Management - Times Series Data Import - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Device Management - Times Series Data Export - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Device Management - BACnet Directory Services - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Device Management - BACnet Directory Services - B |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |

# 9 Data Link Layer

| Support | Listing | Option |
| --- | --- | --- |
| Data Link Layer - MS/TP - Manager Node |  |  |
|  | R | Base Requirements |
|  | C1 | Supports writable Max_Manager property |
|  | C1 | Supports read only Max_Manager property |
|  | C2 | Contains configurable Max_Info_Frames property |
|  | C2 | Contains non-configurable Max_Info_Frames property |
|  | O | Is a BACnet router |
|  | C3,4 | Supports extended MS/TP frames (over 501 octets) |
|  | C5 | Supports the Network Port object |
|  | O6 | Supports configurable Out_Of_Service property |
|  | C7 | Supports hierarchical Network Port objects |
|  | C7 | Supports Non-hierarchical Network Port objects |
|  | C6,8 | Supports writable Network_Number property |
|  | O6 | Supports the Routing_Table property |
|  | O6 | Supports the Network Port object Command property |
|  | O6,9 | Supports the DISCARD_CHANGES command |
|  | O6,9 | Supports the RESTART_SUBORDINATE_DISCOVERY command |
|  | O6,9 | Supports the RESTART_AUTONEGOTIATION command |
|  | O6,9 | Supports the RESTART_PORT command |
|  | O9,10 | Supports the VALIDATE_CHANGES command |
|  | O9,11,12 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Exactly one of these options is required in order to claim conformance to this BIBB. 2 Exactly one of these options is required in order to claim conformance to this BIBB. 3 Protocol_Revision 16 or higher must be claimed. 4 Required if the device is a router and claims Protocol_Revision 16 or higher. 5 Required for devices which claim Protocol_Revision 17. 6 Protocol_Revision 17 or higher must be claimed. 7 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 8 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 9 At least one of these options is required if the Network Port object Command property is supported. 10 Protocol_Revision 24 or higher must be claimed. 11 Protocol_Revision 27 or higher must be claimed. 12 Contact BTL for interim tests for this functionality. |  |  |
| … |  |  |
| Data Link Layer - IPv4 |  |  |
|  | R | Base Requirements |
|  | C1 | Is able to operate in Normal mode |
|  | C1 | Is able to operate in Foreign mode |
|  | C1 | Is able to operate in BBMD mode |
|  | C2 | Supports the Network Port object |
|  | O | Is able to initiate broadcast messages |
|  | O | Supports Network Port objects and DHCP |
|  | O | Supports Network Address Translation in BBMD mode |
|  | O3 | Supports configurable Out_Of_Service property |
|  | C4 | Supports hierarchical Network Port objects |
|  | C4 | Supports Non-hierarchical Network Port objects |
|  | C3,5 | Supports writable Network_Number property |
|  | O3 | Supports the Routing_Table property |
|  | O3 | Supports the Network Port Object Command property |
|  | O3,6 | Supports the DISCARD_CHANGES command |
|  | O3,6 | Supports the RENEW_FD_REGISTRATION command |
|  | O3,6 | Supports the RENEW_DHCP command |
|  | O3,6 | Supports the RESTART_AUTONEGOTIATION command |
|  | O3,6 | Supports the RESTART_PORT command |
|  | O6,7 | Supports the VALIDATE_CHANGES command |
|  | O6,8,9 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Either BBMD or both Normal and Foreign modes are required. 2 This option is required if the IUT claims Protocol_Revision 17 or higher. 3 Protocol_Revision 17 or higher must be claimed. 4 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 5 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 6 At least one of these options is required if the Network Port object Command property is supported. 7 Protocol_Revision 24 or higher must be claimed. 8 Protocol_Revision 27 or higher must be claimed. 9 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - ZigBee |  |  |
|  | R | Base Requirements |
|  | C1 | Supports the Network Port object |
|  | O2 | Supports configurable Out_Of_Service property |
|  | C3 | Supports hierarchical Network Port objects |
|  | C3 | Supports Non-hierarchical Network Port objects |
|  | C2,4 | Supports writable Network_Number property |
|  | O | Supports the Routing_Table property |
|  | O | Supports the Network Port Object Command property |
|  | O2,5 | Supports the DISCARD_CHANGES command |
|  | O2,5 | Supports the RESTART_AUTONEGOTIATION command |
|  | O2,5 | Supports the RESTART_PORT command |
|  | O5,6 | Supports the VALIDATE_CHANGES command |
|  | O5,7,8 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Required if the IUT claims Protocol_Revision 17 or higher. 2 Protocol_Revision 17 or higher must be claimed. 3 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 4 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 5 At least one of these options is required if the Network Port object Command property is supported. 6 Protocol_Revision 24 or higher must be claimed. 7 Protocol_Revision 27 or higher must be claimed. 8 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - Ethernet |  |  |
|  | R | Base Requirements |
|  | C1 | Supports the Network Port object |
|  | O2 | Supports configurable Out_Of_Service property |
|  | C3 | Supports hierarchical Network Port objects |
|  | C3 | Supports Non-hierarchical Network Port objects |
|  | C2,4 | Supports writable Network_Number property |
|  | O | Supports the Routing_Table property |
|  | O | Supports the Network Port Object Command property |
|  | O2,5 | Supports the DISCARD_CHANGES command |
|  | O2,5 | Supports the RESTART_AUTONEGOTIATION command |
|  | O2,5 | Supports the RESTART_PORT command |
|  | O5,6 | Supports the VALIDATE_CHANGES command |
|  | O5,7,8 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Required if the IUT claims Protocol_Revision 17 or higher. 2 Protocol_Revision 17 or higher must be claimed. 3 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 4 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 5 At least one of these options is required if the Network Port object Command property is supported. 6 Protocol_Revision 24 or higher must be claimed. 7 Protocol_Revision 27 or higher must be claimed. 8 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - ARCNET |  |  |
|  | R | Base Requirements |
|  | C1 | Supports the Network Port object |
|  | O2 | Supports configurable Out_Of_Service property |
|  | C3 | Supports hierarchical Network Port objects |
|  | C3 | Supports Non-hierarchical Network Port objects |
|  | C2,4 | Supports writable Network_Number property |
|  | O | Supports the Routing_Table property |
|  | O | Supports the Network Port Object Command property |
|  | O2,5 | Supports the DISCARD_CHANGES command |
|  | O2,5 | Supports the RESTART_AUTONEGOTIATION command |
|  | O2,5 | Supports the RESTART_PORT command |
|  | O5,6 | Supports the VALIDATE_CHANGES command |
|  | O5,7,8 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Required if the IUT claims Protocol_Revision 17 or higher. 2 Protocol_Revision 17 or higher must be claimed. 3 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 4 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 5 At least one of these options is required if the Network Port object Command property is supported. 6 Protocol_Revision 24 or higher must be claimed. 7 Protocol_Revision 27 or higher must be claimed. 8 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - LonTalk |  |  |
|  | R | Base Requirements |
|  | C1 | Supports the Network Port object |
|  | O2 | Supports configurable Out_Of_Service property |
|  | C3 | Supports hierarchical Network Port objects |
|  | C3 | Supports Non-hierarchical Network Port objects |
|  | C2,4 | Supports writable Network_Number property |
|  | O | Supports the Routing_Table property |
|  | O | Supports the Network Port Object Command property |
|  | O2,5 | Supports the DISCARD_CHANGES command |
|  | O2,5 | Supports the RESTART_AUTONEGOTIATION command |
|  | O2,5 | Supports the RESTART_PORT command |
|  | O5,6 | Supports the VALIDATE_CHANGES command |
|  | O5,7,8 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Required if the IUT claims Protocol_Revision 17 or higher. 2 Protocol_Revision 17 or higher must be claimed. 3 At least one of these options is required if the IUT claims Protocol_Revision 17 or higher. 4 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 5 At least one of these options is required if the Network Port object Command property is supported. 6 Protocol_Revision 24 or higher must be claimed. 7 Protocol_Revision 27 or higher must be claimed. 8 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - IPv6 |  |  |
|  | R | Base Requirements |
|  | C1 | Is able to operate in Normal mode |
|  | C1 | Is able to operate in Foreign mode |
|  | C1 | Is able to operate in BBMD mode |
|  | R | Supports the Network Port object |
|  | O | Supports DHCP |
|  | O | Supports configurable Out_Of_Service property |
|  | C2 | Supports hierarchical Network Port objects |
|  | C2 | Supports Non-hierarchical Network Port objects |
|  | C3 | Supports writable Network_Number property |
|  | O | Supports the Routing_Table property |
|  | O | Supports the Network Port Object Command property |
|  | O4 | Supports the DISCARD_CHANGES command |
|  | O4 | Supports the RENEW_FD_REGISTRATION command |
|  | O4 | Supports the RENEW_DHCP command |
|  | O4 | Supports the RESTART_AUTONEGOTIATION command |
|  | O4 | Supports the RESTART_PORT command |
|  | O4,5 | Supports the VALIDATE_CHANGES command |
|  | O4,6,7 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 Either BBMD or both Normal and Foreign modes are required. 2 At least one of these options is required. 3 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 4 At least one of these options is required if the Network Port object Command property is supported. 5 Protocol_Revision 24 or higher must be claimed. 6 Protocol_Revision 27 or higher must be claimed. 7 Contact BTL for interim tests for this functionality. |  |  |
| Data Link Layer - Secure Connect |  |  |
|  | R | Base Requirements |
|  | C1 | Is able to operate as a node without a local hub function |
|  | C1 | Is able to operate as a hub |
|  | O | Supports direct connections |
|  | O2 | Is able to accept direct connections |
|  | O2 | Is able to initiate direct connections |
|  | C3 | Supports the Network Port object |
|  | C4 | Contains a Network Port object with a Proprietary Network_Type |
|  | C5 | Supports DM-TS-B |
|  | C5 | Supports DM-UTC-B |
|  | C5 | Supports Time Synchronization by Some Other Method |
|  | C6 | Supports B/SC over IPv4 |
|  | C6 | Supports B/SC over IPv6 |
|  | O7 | Supports configurable Out_Of_Service property |
|  | C7,8 | Supports hierarchical Network Port objects |
|  | C7,8 | Supports Non-hierarchical Network Port objects |
|  | C7,10 | Supports writable Network_Number property |
|  | O7 | Supports the Routing_Table property |
|  | O7 | Supports the Network Port Object Command property |
|  | O7,9 | Supports the DISCARD_CHANGES command |
|  | O7,9 | Supports the RESTART_PORT command |
|  | O9,11 | Supports the GENERATE_CSR_FILE command |
|  | O9,11 | Supports the VALIDATE_CHANGES command |
|  | O9,12,13 | Supports the RESTART_DEVICE_DISCOVERY command |
| 1 At least one of these options must be supported. 2 At least one of these options must be supported if the device supports direct connections. 3 Required if the IUT claims Protocol_Revision 24 or higher. 4 Required if the IUT claims a Protocol_Revision greater than 16 and less than 24. 5 At least one of these options must be supported. 6 At least one of these options must be supported. 7 Protocol_Revision 17 or higher must be claimed. 8 At least one of these options must be supported. 9 At least one of these options is required if the Network Port object Command property is supported. 10 Support for writable Network_Number properties is required in routers and other IUTs that need to know the network number in order to operate. 11 Protocol_Revision 24 or higher must be claimed. 12 Protocol_Revision 27 or higher must be claimed. 13 Contact BTL for interim tests for this functionality. |  |  |
| … |  |  |

# 14 BACnet Web Services

| Support | Listing | Option |
| --- | --- | --- |
| BACnet Web Services Client |  |  |
|  | R1 | Base Requirements |
|  | O1,2 | Supports BACnet Energy Services Interface |
| 1 Contact BTL for interim tests for this functionality. 2 Protocol_Revision 30 or higher must be claimed. |  |  |
| … |  |  |

# XX Authentication and Authorization

| Support | Listing | Option |
| --- | --- | --- |
| Authentication and Authorization - Dynamic Authorization Client - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Authentication and Authorization - Static Authorization Client - A |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Authentication and Authorization - Authorization Target - B |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |
| Authentication and Authorization - Non-secure Authorization Target - B |  |  |
|  | R1 | Base Requirements |
| 1 Contact BTL for interim tests for this BIBB. |  |  |

| Version | Date | Author | Change |
| --- | --- | --- | --- |
| 26.0 - 1.0 | 2024-12-20 | Michael Osborne | Initial Release. Supports Test Package 26.0. |
| 26.0 - 2.0 | 2025-03-24 | Michael Osborne | BTLWG-1683 - Add Virutual Data Link to the Test Package |
| 26.0 - 3.0 | 2025-07-24 | Michael Osborne | BTLWG-1729 - B/SC Checklist for pre-PR24 NPOs Does not Allow routing BTLWG-1733 - Test for src port <> dst port BRLWG-1746 – Relinquish non-commandable properties BTLWG-1760 – PR 27 to 30 Checklist Items |
| 26.1 – 1.0 | 2025-11-17 | Michael Osborne | Removed all but BTLWG-1760 Update Clause 9 to match TP26.1 |
| 26.1 - 2.0 | 2026-03-19 | Michael Osborne | Add DM-TSDI-A and DM-TSDE-A Added Directory Services (PR 31) |